WIMBORNE MODEL TOWN
DEVELOPMENT
RIVER SYSTEM: CONTROL STRATEGY
DESIGN DOCUMENT
Issue 0.4
6th August 2019

This work is licensed under the Creative Commons Attribution-NonCommercial-ShareAlike 4.0 International License. To view a copy of this license, visit http://creativecommons.org/licenses/by-nc-sa/4.0/.

# INTRODUCTION
## Background
Work on the Wimborne Model Town Water Sustainability Project has now entering its third year, and a partially working system has been realised using a number of techniques.
The referenced documents in Table 1 below provide a definition of the system design and implementation at the time that this document was released.
The aim of this document is to provide an agreed approach to the control of the various devices in the system in the light of the understanding gained during the development activities over the past two years, so that the strategy may be translated into a fully working system.
Reference 2.5 below provides a number of diagrams that show how the system will be physically implemented when the project is complete.
## Current Status
### Hardware
With the exception of the Visitor / Staff GUI and the Database Server (a Network Attached Storage Box (NAS), see below), the hardware development has largely been completed. It is known that the Sensor and Control Interface for the Lady Hanham Butts Group will require enhancements to cope with additional probes, but all device types have now been designed, built and deployed. The current system has now been working well for some time.
At the time that this document was written, this system consists of:
- Sensor and Control Interfaces.
  - These are installed at:
    - The Sump.
    - The Wendy Street Butts.
    - The Stage Butts.
  - Each Sensor and Control Interface can cater for one or more of the following peripheral devices:
    - Hall-Effect Level Probe.
    - Float Switch to detect the Butts are full.
    - Solid State Relay (SSR) to operate mains powered pumps.
- One Gate Valve at the Wendy Street Butts.
### Software
The ‘Software Framework’ provides a scalable platform for expanding the current working solution to accommodate a larger system. Apart from the NAS Box, the Matrix Pump and (to a much lesser extent) the Lady Hanham Butts Sensor and Control Interface, the software components to create this already exists.
However the availability of a surplus NAS Box for the project has opened up new possibilities and triggered a rethink on the implementation of the code. One of the main reasons for producing this document is to create a good definition of how the new control strategy will work and what that means with respect to the current code.
For the deployed system, measured values and control signals are passed over an Ethernet network using an implementation of sockets code. However, with the provision of the Database Server, an alternative strategy has been proposed and this is outline below.
# RELATED DOCUMENTS
The following documents are related to this document.
Table 1: Related Documents
No	Requirement	Iss
1	WMT – Development – River System Software Requirements	0.2
2	WMT – Development – River System Phase 4 Design Document	0.5
3	WMT – Software API Documentation	For software v0.11.0~pre2 (In active development)
4	WMT – Development – River System Phase 4 Installation Specification	0.4
5	WMT – River System Overall System Configuration	0.10
6	WMT - River System Software Design Specification	0.7

# CONTROL STRATEGY
## Overall Approach
The key requirements of the control systems are:
- To only add mains water when there is no stored water available.
- To ensure that stored water is distributed efficiently to avoid overflowing when storage space is still available.
This will be achieved by dividing the responsibilities for control into zones, so the Sump and Wendy Butts zone remains largely as it is in the currently deployed system and the water in the Stage Butts zone and the Lady Hanham Butts zone is controlled by their associated Pis, as described below. Referring to Page 3 of Reference 2.5:
- When the weather is dry, water will move down from G1, G2 and G3 in the Lady Hanham Butts Group G4 at the Wendy Butts. This movement would be aided by the Matrix pump.
- In extremely dry conditions, when none of the Butts Groups have water, but before the Sump runs dry, then a solenoid valve would allow mains water into the Lady Hanham Butts Groups.
- When the weather is wet, water will be pumped from G4 to G3, G2, and G1.
Water in the Stage Butts will be managed in a similar (albeit simpler) way. Water in the Gazebo Butts will not be part of the overall control loop and will be furnished with a manual control on the Staff GUI or will carry out automatic watering, via a soaker hose. This will be triggered by a moisture sensor in the soil or by a knowledge of weather conditions. The Gazebo Butts Group is likely to be the last system to be commissioned and advice will be sought from the gardeners as to their requirements,
## Detailed Approach
### High-Level Control Algorithm in Each zone
The control algorithms required at each Butts Group will be different because there are different devices attached to each Pi. In particular the algorithm for the Lady Hanham Butts Group will have to evaluate readings from three combined float switches and three Hall Effect Probes and then control the positions of three Gate Valves and a mains solenoid valve to achieve the requirements outlined above.
It is intended that a flowchart will eventually be produced and either included in this document or in the Software Design Specification (Reference 2.6) to describe the detailed design strategy for these algorithms, in the meantime, the following description outlines the details.
Each control Pi, eg (Sump, Stage, Wendy, Lady Hanham and Gazebo) will monitor and record the water levels in their designated zone. The algorithm for the Sump/Wendy Butts zone will remain largely as it is and the other Pis will mimic what that zone does, with enhancements as needed, eg:
In the Stage Butts zone (G6), the Pi will keep track of the water level in it's own Butts and also of the level in the Wendy Butts (G4):
  - If Wendy Butts are low and Stage Butts have water, the Pi will open the Stage Butts Gate Valve (V12) and turn on the Matrix Pump to fill the Wendy Butts, eg pumping downwards.
  - If Wendy Butts are high and Stage Butts low, the Pi will open V12 and turn on the Matrix Pump to fill the Stage Butts, eg pumping upwards
  - Once G4 has reached the desired level, or the Stage Butts have no more water, then V12 will be closed and the Matrix Pump will be disabled.
- In the Lady Hanham Butts zone (G1, G2 and G3), the Pi will keep track of the water level in it's own Butts and also the level in the Wendy Butts (G4):
  - If Wendy Butts are low and Lady Hanham Butts have water, the Pi will open the Lady Hanham Gate Valve(s) and turn on the Matrix Pump to fill the Wendy Butts, eg pumping downwards.
    - In order to comply with the key requirement of only adding mains water when there is no stored water available:
      - Water in G3 will be used to fill G4 by opening V3.
      - Then, water in G2 will be used to fill G3 by opening V2.
      - Then, water in G1 will be used to fill G2 by opening V1.
      - Mains water will only be added if G1, G2 and G3 are empty and G4’s water level is low (eg less than 400 mm).
      - Once G4 has reached the desired level, or there is no more water in G1, G2 or G3, then V1, V2, V3 will be closed and the Matrix Pump will be disabled.
  - If Wendy Butts are high and Lady Hanham Butts low, the Pi will open the Lady Hanham Gate Valve(s) and turn on the Matrix Pump to fill the Lady Hanham Butts, eg pumping upwards.
    - In order to comply with the key requirement of avoiding overflowing of the system when storage space is still available:
      - Water in G4 will be used to fill G3 by opening V3
      - Water in G3 will be used to fill G2 by opening V2.
      - Water in G1 will be used to fill G2 by opening V1.
By a system of ‘software locks’, access to the key shared components, the the gate valves and pump in the Matrix Pump will be made available, see Section 4.1.1 below.
Gazebo Butts only has to turn on the soaker hose when there is sufficient water and it is demanded by the Staff GUI or by an automatic or timed event.
During development, the system will be tuned and high and low levels that define ‘empty’ and ‘full’ will be set which trigger the filling actions.

# NEW AND MODIFIED TECHNIQUES
## New Techniques
### Use of the Database Server
As described in Section 1.2.2, the current system employs sockets code to make levels and control states available to the ‘Master Pi’ eg Sump Pi. Each Pi then runs an algorithm to determine when to open valves or enable pumps.
This works well, but it is uncertain if it will scale well. The current system only includes three Master and Remote Pi Interfaces and one Gate Valve, whereas the final system will contain five Sensor and Control Interfaces (a rename of the Master and Remote Pi Interfaces) and eleven Gate Valves. Furthermore each zone’s Pi will need to work independently of the others, with its decisions being based solely on the levels of water in the Butts Groups inside it’s zone and in the G4 zone.
The availability of a NAS Box provides the opportunity of largely dropping the sockets code to obtain level and status data. At this stage of development it is accepted that sockets code may still needed to transmit reading intervals and system ticks, because these are time-sensitive, unlike other data. Without this, any slow-down on the database server may impact reliability of the system.
It is possible that using the database server to store and compute all of the data needed centrally may overload the NAS Box, which has a relatively low-power CPU and limited memory, so other functions may also have to revert to the Pis and a ‘master’ Pi may have to be re-instated.
Each Pi will monitor the levels, etc in it’s zone by reading sensors and writing the results to the database. Then, each Pi will also monitor the levels in adjacent zones by reading the database. Using the dedicated algorithm for that zone, each Pi will then control pumps and Gate Valves to maintain the levels detailed in the previous Section and ensure that water is always available in G4 to replenish the Sump.
Other data will also be written to the database, including:
- Datestamp. This will be the time that the Pi obtained the level from the probe, so will be slightly different to the time taken by other Pis at roughly the same time.
- ‘System Tick’ to be used to synchronise readings within a time-frame.
- The current position of Gate Valves.
- The state of pumps, eg, pumping up, pumping down and idle.
This additional data will, for example, allow a ‘lock’ condition to be implemented in the Software Framework, thus preventing another Pi from attempting to take control of the device while it is busy.
### State Modelling
One lesson learned from the current implementation is that some state modelling will be required to optimise the system. As it stands, the Butts Pump will be turned on if the Sump has more than a certain amount of water and the Wendy Butts have less than a similar amount. Similarly, the G4 Gate Valve will be opened if the Wendy Butts have more than a certain amount of water and the Sump has less than a similar amount. The result of this is that under edge conditions, when the levels are close to the specified limits, the software tends to oscillate between pumping and opening the Gate Valve.
What is really needed is that if the Sump is fairly full, the Butts Pump will be turned on until either the Butts are full or the water in the Sump falls below a much lower level. Similarly, the Gate Valve will be opened when the Wendy Butts are fairly full until either the Sump is full or the water in the Butts falls below a much lower level. To do this, it is necessary for the direction of the water level in the vessel to be stored in the database along with the value, eg rising and falling. This function will be computed by the NAS Box unless it is overloaded.
### System Startup
Another lesson learned from the current implementation is that when the system boots up (after a power outage for example) there may be a significant period of time before the true level values are recorded. This is because the Hall Effect Probes generate an out-of-limits value if the float is between sensors and the software interprets this as invalid and (currently) returns a value of 0 mm.
If the Gate Valve is closed and the Pump off, then it could be some hours before the level changes in the vessel and a true measurement is obtained. During this period, the system is effectively ‘out-of-control’ and water may be lost or the Sump may run dry.
To help combat this, a Combined Float Switch has been developed. This has two micro-switches; one performs the same function as the current single action float switch and signals the Pi when the Butts are full. The second microswitch switch will generate a signal to the Pi when the Butts are empty.
At startup, each Pi will:
1. Turn all pumps off and close all valves.
2. Immediately write the levels read from all of its sensors to the database.
  1. If the Max Float Switch in a vessel is True enter a level of 700 mm in the database.
  2. If the Min Float Switch in a vessel is True enter a level of 0 mm in the database.
  3. Otherwise write the actual reading from the Hall-effect Probe, unless the float is ‘between levels’ when the returned value for that probe will not be a true value and there will be an indeterminate level in the record for that device.
3. With this potentially incomplete status view the following algorithm will be used to fill in the gaps:
  1. If the vessel has a measured value of < 200 mm or indeterminate, open a Gate Valve from the Butts Group above the vessel and enable the Matrix Pump to move water downwards into the vessel. Continue until a measured value is recorded. (In the case of the Sump, then V4 will be opened and gravity used to move the water.)
  2. If the vessel has a measured value > 300 mm or an indeterminate value still exists, open a Gate Valve from the Butts Group above the vessel and enable the Matrix Pump to move water upwards from the vessel. Continue until a measured value is recorded. (In the case of the Sump, then the Butts Pump will be started).
  3. For a Sump level only, if the above measures fail to establish the levels, turn off the Main Circulation Pump. This will allow water in the River System to fill the Sump and a measured value to be recorded.
2. If none of the foregoing results in a reading, close all valves and open the mains feed solenoid until the associated Lady Hanham sensor records a reading. Re-run the Startup sequence above to ensure that all sensors are providing valid readings.
3. If invalid readings still exist, then request human intervention through the Staff GUI or by some other (TBD) means.
  1. In this circumstance staff should open the Lady Hanham valves (V1, V2, V3) to equalise the water level in G1, G2 and G3 and wait until valid measurement values are recorded for each Lady Hanham probe.
  2. Turn off the mains feed solenoid, close valves and revert to automatic operation..
### System Tick
The System Tick will be generated by the NAS Box (unless this results in overloading) which will generate a number that increments over an agreed interval that is less than the shortest reading interval, eg 10 seconds. This number will be made available to all the Pis, either by being written to a known record in the database or via sockets code of the performance of the NAS Box limits the response times. If the former solution is selected then the value will be overwritten each time the new number is generated.
Each Pi will read this number and write it to each record written to the database.
### Watchdog Feature
A ‘Watchdog’ feature will be implemented in each Pi to generate a status record in the database on a regular basis so that other devices in the system can identify faults and attempt to heal them. There will be several levels of this:
1. A Watchdog timer will be set within the main loop of the Software Framework and reset each time the software completes a loop. If the timer is reset, the status record in the database will be updated. If the timer counts down to zero, then two things will be known:
  1. The Pi is still executing the program:
  2. The program is locked or stalled in a subsidiary thread.
In this instance the exception handler in the Watchdog routine will stop execution of the software and restart it. A (Level 1) Warning symbol will be shown on the Staff GUI and another (TBD) method will be used to alert the staff.
If the previous Watchdog fails to detect a locked-up program, then an external Watchdog routine will take over, having allowed sufficient time for the internal Watchdog to detect the problem and restart the code. This program will monitor the Pi’s status record on the NAS Box and if it is not updated regularly, then it will be known that the program has failed.
In this instance the exception handler in the external Watchdog routine will stop execution of the software and restart it. A (Level 2) Warning symbol will be shown on the Staff GUI and another (TBD) method will be used to alert the staff.
If the previous method fails, then a third Watchdog function running as a bash script, or by some method independent of Python, will examine the Software Framework’s process status to ensure that it is not completely idle or has become a zombie.
In this instance the code in the script will trigger a reboot of the faulty Pi.
If all of the previous Watchdog solutions fail to detect a locked-up program, then a fourth external Watchdog program, running on the NAS Box, will detect it by monitoring the status records written by the Pis.
In this instance the exception handler in the NAS Box Watchdog routine will trigger a reboot of the faulty Pi.
NOTE:	It is expected that this final Watchdog feature is likely to be implemented last and will have a low priority at this time.
# DEVELOPMENT ACTIVITIES TO BE CARRIED OUT
The activities detailed below will all be needed to realise the completed solution. They can be carried out in any order, but have been written on a logical progression.
## Software Framework
### Cater for the Combined Float Switch
After the necessary hardware modifications to the Sensor and Control Interface have been completed, the signal from the new switch will be pulled-up and routed to an additional GPIO Pin. The new switch is wired internally to generate a low when the vessel has water and a high when it doesn’t. This new capability will need supporting.
### System Startup
Code to implement the strategy described in Section 4.1.3 above will need to be incorporated and run when the system is first booted.
### State Modelling
The current algorithms (encapsulated in the sumppi_control_logic() function in the deployed system) will require updating to detect whether the level in the vessel is rising or falling, unless the NAS Box can perform thi function.
### Watchdog
This is a completely new capability and may well be left until the main algorithms are functioning correctly. However, it should be implemented as soon as possible after that to improve the fail-over performance and to alert the WMT Staff when a fault occurs that cannot be self-healed.
## Database Server
A significant amount of work has already been completed on preparing the NAS Box to provide the database capability required. The following activities need to be completed:
### Database Schema
The database schema will be developed and agreed before building the system. The format of this schema is TBD, but a simple table or diagram may suffice. The use of free online tools might also be a possibility, such as mySQL Workbench from Oracle (it requires an Oracle account, but it’s free to download.
It is not envisaged that the schema would be particularly complex and would probably consist of the following Records, structured to provide the required content and using the standard:
Record Type	Identity	DateStamp	System Tick	Value
Hall Effect Probe	SUMP:M0	2019-08-01 11:30:42	123456	450
Hall Effect Probe	G4:M0	2019-08-01 11:30:51	123456	450
Gate Valve	V4	2019-08-01 11:31:21	123456	20
etc

Other schema elements may be required.
### Database Construction
Using the agreed schema, the database will be constructed to provide all of the records and elements needed.
## Integration of the Database
### Database Interaction
Once the database schema has been used to construct the database, the Software Framework code will require modification so that the measured values and device status strings are written to the database rather than the sockets layer.
Integration will then be required before the complete system is deployed.