WIMBORNE MODEL TOWN
DEVELOPMENT
RIVER SYSTEM REQUIREMENTS
Issue 0.4.1
19th April 2016

This work is licensed under the Creative Commons Attribution-NonCommercial-ShareAlike 4.0 International License. To view a copy of this license, visit http://creativecommons.org/licenses/by-nc-sa/4.0/.

# INTRODUCTION
This document details the requirements for a number of enhancements to the Wimborne Model Town River feature.
## BACKGROUND TO THE REQUIREMENTS
WMT has embarked on an ambitious multi-phase programme to reduce the dependence of the Model Town and Gardens on mains water. Previously mains water was exclusively used to supply the model river system and for plant irrigation.
The programme is intended to have environmental benefits through its approach to sustainable water use and also to provide an educational platform, on a number of levels, to inform our visitors on topics like: the eco-system created; the technology utilised; the sustainability benefits; cost savings; and so forth.
It has been decided to undertake the programme in phases so as to cause minimal disruption to WMT as a visitor attraction and to align the affordability of our overall goal to the budgetary constraints of the charitable trust that runs it
### How Things Were
Mains water was used exclusively to fill the river system as the start of each season and to top it up when its water level dropped below that necessary to maintain a minimum water flow.
The river system itself suffered from a number of problems:
1. Water flow was low.
2. There was no water filtration
3. There was excessive algae growth
4. Water quality was poor
5. Water was lost due to numerous leaks
6. Maintaining correct water levels needed excessive manual intervention
7. Any excess water, from rainfall, was lost when the rivers capacity was exceeded.
While some attempt was made to harvest some rainwater from building roofs, which was fed into the river system in an uncontrolled way, any rainwater beyond the rivers capacity to hold it was lost as overflow into soak-aways.
A water butt was utilised in the plant potting area, but for general irrigation there was no alternative but to use hoses connected to mains water. The number and location of mains water taps was also an issue for the gardeners.
## Related Documents
The following documents have been used as the source materials for these Requirements.
Table 1: Related Documents

No	Requirement	Issue / Date
1	Water Sustainability at WMT - (reducing dependance on Mains Water)	6th April 2017
2	WMT River System (System Diagram)	1.0
3	WMT River System (Visitor Information)	1.0
4	River Layout	1.1
5	River Capacity	1.0
6	Wimborne Model Town Development – River System: Phase Requirements	0.2

# TOP-LEVEL REQUIREMENTS
The following Top-level requirements have been identified.
## Primary
Maintain a water flow in the river system at all times; sufficient to ensure water clarity and inhibit algae growth.
Note 1:	The link between slow moving / stagnant water and algae growth has been made in literature but it is conjecture that it is the cause of WMT’s river system’s problem.
1. Reduce the dependence of the river system on mains water.
2. Enhance WMT as a visitor attraction.
3. Enhance the educational value of the WMT.
## Secondary
Provide a source of harvested rain water that can be used to irrigate the gardens.
Note 2:	In the past irrigation was by spraying with hosepipes, it is now planned to also introduce soaker hoses into some of the planting areas.
1. Expand rain water harvesting, storage and irrigation feeds to suit needs of river / gardens.
2. Stored water “balancing” between storage sites.
# DERIVED REQUIREMENTS
The following requirements have been derived from the Top-Level requirements. These are split into the proposed phased approach to the work. The following Notes apply:
Notes:
1.	Requirements have been derived from various source documents detailed in Section 1.2 above.
1a.	Reference Numbers in bold are taken from the Top-Level Requirements in Section 2 above and have been included in the column headed ‘Source’.
1b.	Other Reference Numbers are taken from Related Document 1 in Section 1.2.
2.	Some of the Requirements have already been fulfilled under previous agreements and these are marked ‘Completed’ in the Tables below. They are included so that this document may provide a full picture of the Project.
## Functional
The functionality required of each element of the system during each Phase is detailed in Related Document 6 (see Section 1.2. This document provides the requirement, it's priority, its type and its status. Top-level Requirements are highlighted, so that the origin of the Derived Requirements may be identified.
The Phases have been identified as:
Phase 1 – Cleaning, Clearing and Flow Improvement
Phase 2 – Improve Water Clarity and the WMT as a Visitor Attraction
Phase 3 – Reduce the Dependence of the River System on Mains Water
Phase 4 – Automate the System
Phase 5 – Expand Rainwater Storage and Irrigation
Phase 6 – Stored Water Balancing Between Storage Sites
## Operational
The Table below details the operational capabilities required of the system, it's priority and type.
Table 2: Operational Requirements

No	Requirement	Priority	Type
2.1	The system shall be designed so that the Town staff can start the pumping and filtration system by turning on the power.	1	Essential
2.2	The system shall be designed so that the Town staff can stop the pumping and filtration system by turning off the power.	1	Essential
2.3	Manual control of the pumping and filtration system shall be provided.	1	Essential
2.4	Automatic control of the various functions shall be transparent to the Town staff, except when manual override is necessary.	1	Essential
2.4.1	Manual control of the automated functions shall be available to the Town staff via a standard computer in the WMT Office	2	Desirable
2.5	The educational display detailed in Requirement No 3.1.4.4 shall be provided in a form that allows the Visitors to monitor the following functions:	2	Desirable
2.5.1	Water flow through supply pipe.	2	Desirable
2.5.2	Water flow in the river.	2	Desirable
2.5.3	Height of water in the sump.	2	Desirable

## Environmental
The Table below details the environmental requirements of the system, their priority and type.
Table 3: Environmental Requirements

No	Requirement	Priority	Type
3.1	The system must not pollute the river water or any other part of the environment.	1	Essential
3.2	All electronic components of the system that are installed as part of Phase 4 shall be protected from the ingress of moisture.	1	Essential
3.3	All electronic components shall be adequately cooled.	1	Essential

## Reliability
The Table below details the reliability required of the system, it's priority and type.
Table 4: Reliability Requirements

No	Requirement	Priority	Type
4.1	The system shall be designed to be fail-safe in the event of a power supply failure.	1	Essential
4.2	Components shall be de-rated where possible, especially circuits carrying powers in excess of 1 W.	1	Essential
4.3	The system shall use redundancy where possible to protect against hardware failures.	2	Desirable
4.4	If the sump runs out of water, the system must immediately take action to avoid damage to the main pump.	1	Essential

## Maintainability
The Table below details the maintainability required of the system, it's priority and type.
Table 5: Maintainability Requirements

No	Requirement	Priority	Type
5.1	The system shall be designed to be maintainable by suitably qualified Town staff, using only the documentation provided by the developers.	1	Essential
5.2	Spares shall be provided for any components that are liable to end-of-life or frequent failure.	1	Essential
5.3	Backups of any software developed shall be made available for future maintainers.	1	Essential
5.4	As far as possible, the system shall keep its system software up to date automatically in the light of security issues.	1	Desirable

## Safety
The Table below details the safety requirements of the system, it's priority and type.
Table 6: Safety Requirements

No	Requirement	Priority	Type
6.1	The system must be designed such that elements of the system that use mains or high voltage supplies are fully protected to avoid the danger of electrical shock.	1	Essential
6.2	Power supplies derived from mains must be fully enclosed in a protective case.	1	Essential
6.3	Any heavy objects, such as the water butts, must be adequately secured to prevent inadvertent injury.	1	Essential

## Documentation
The Table below details the documentation requirements of the system, it's priority and type.
Table 7: Documentation Requirements

No	Requirement	Priority	Type
7.1	A comprehensive design specification shall be produced.	1	Essential
7.2	The design specification shall include full descriptions of all functionality, parts lists and circuit diagrams.	1	Essential
7.3	All software shall be fully documented with comments.	1	Essential
7.4	An Installation Specification shall be provided that details how to deploy the software and hardware.	1	Essential
7.4.1	A set of installation scripts shall be provided where possible to automate large parts of the software setup process.	2	Desirable
7.5	A User Manual shall be provided that details how to use and maintain the software and hardware.	1	Essential

## Miscellaneous
The Table below details the miscellaneous requirements of the system, it's priority and type.
Table 8: Miscellaneous Requirements

No	Requirement	Priority	Type
8.1	Where possible and without compromising the other requirements in this document, elements of the existing system shall be re-used.	2	Goal
8.2.	The project team shall estimate the cost of each phase of the project, so that a budget may be agreed.	2	Goal
8.3	The project shall be developed in an agile manner so that the order of development may be varied to suit budgetary constraints and opportunities.	2	Goal

# ASSUMPTIONS
The following assumptions are made.
- Developers will have the pre-requisite knowledge to design and implement the hardware and software required to realise this project and subsequently enhance it.
- Maintainers will have the pre-requisite knowledge, supported by the supplied documentation, to maintain the system.
- WMT staff will have the pre-requisite knowledge, supported by the supplied documentation, to operate and monitor the system.