WIMBORNE MODEL TOWN
DEVELOPMENT
RIVER SYSTEM SOFTWARE REQUIREMENTS
Issue 0.1
26th September 2017

This work is licensed under the Creative Commons Attribution-NonCommercial-ShareAlike 4.0 International License. To view a copy of this license, visit http://creativecommons.org/licenses/by-nc-sa/4.0/.

Annexes
A	Illustrations

# INTRODUCTION
This document details the requirements for the software to control and monitor pumps, valves and sensors in the Wimborne Model Town River feature. This version of the document covers the Requirements for the software associated with the prototype development carried out over the summer and autumn of 2017. This development is intended to:
- Monitor the level of water in the sump.
- Switch on and off a pump to transfer water from the sump to five butts installed behind the Wendy House.
- Ensure that the butts do not overflow by monitoring the state of a float switch which indicates that they full.
To maintain a constant replenishment of the sump as water is lost from the system by leakage and evaporation, a slow flow of water from the butts to the sump shall be maintained by partially opening a manual valve.
## BACKGROUND TO THE REQUIREMENTS
Full details of the background to the Requirements for the enhancements to the river system as a whole may be found in Reference 1 in Section 1.2.
## Related Documents
The following documents are relevant to these Requirements.
Table 1: Related Documents

No	Requirement	Issue / Date
1	WMT River System Requirements	0.5
2	Hall-effect Sensor (http://wmtprojectsforum.altervista.org/forum/viewtopic.php?f=15&t=37#p565)	-

## Definitions
buttspi	The complete hardware and software installation at the Butts (see Illustration 1).
master	The Raspberry Pi that is controlling the system.
SSH	Secure Shell. Used to log in to the Pis from another device.
sumppi	The complete hardware and software installation at the Sump (see Illustration 1).
remote	Any Raspberry Pi that is under the control of the master.

# GENERAL REQUIREMENTS
The following software requirements have been identified.
## Hardware Configuration
Figure 1 in Annex A shows the general arrangement of the hardware for the prototype deployment.
## Software Environment
The Operating System shall be Raspbian version Stretch.
## Communications
All communications between sumppi and buttspi shall be via the Ethernet link. For this deployment, a Wireless Access Point will allow communication with both Pis from a laptop of mobile phone. This will be removed from the final deployment.
# FUNCTIONAL REQUIREMENTS
## Functional Software Requirements for sumppi
For the prototype deployment, sumppi has only one probe connected; a level sensor based on hall effect devices. As the water level changes, a group of magnets attached to a float generate a signal in adjacent hall-effect sensors. These signals are turned into a logic voltage. The sensor signals are Active-Low, so the input to the Interfacing Board is 0 V when the magnet is close to a sensor and 5 V when it is not.
Table 2: sumppi Functional Requirements

No	Requirement
2.4.1	sumppi shall be the master Pi.
2.4.2	Monitor the level of the water in the sump frequently by reading the outputs of the Resistance Probe.
2.4.3	Write the results of the sump level measurements to a local file for future analysis and diagnostic purposes.
2.4.4	Establish communications between itself and buttspi.
2.4.5	Monitor buttspi frequently to monitor the level of water in the Butts.
2.4.6	Using the results obtained from the level measurements, operate the butts pump to maintain the level of the water in the sump between <Low Level> mm and <High Level> mm.
2.4.7	Suspend pumping of water to the Butts if the Float Switch is actuated, signalling that the Butts are full.

Notes:
1. <Low Level> mm and <High Level> mm will be determined during development, but are assumed to be between 400 mm and 600 mm initially.
2. If possible, a background pumping level should be maintained, so that under stable conditions the Butts Pump is enabled at regular intervals to keep the sump water level close to <High Level>, but without exceeding it. In other words the average rate of flow of water from the Sump to the Butts should equal the rate of flow from the Butts to the Sump. It is recognised that the flow into the sump will reduce as the level of water in the Butts decreases, so the final algorithm should take this into account.
3. When the Butts are full, then no more water will be pumped out of the sump, so the excess will be lost through the overflow into the soakaway.
## Functional Software Requirements for buttspi
For the current deployment, buttspi has only got one probe connected, a float switch. As the water reaches the top of the Butts a microswitch is made. The probe is Active-Low, so the input to the Interfacing Board is 0 V when the float switch is closed and 5 V when it is open.
Table 3: buttspi Functional Requirements

No	Requirement
2.5.1	buttspi shall be the remote Pi.
2.5.2	Monitor the state of the float switch frequently.
2.5.3	Write the results of the float switch state to a local file for future analysis and diagnostic purposes.
2.5.4	Establish communications between itself and sumppi by responding on the network to packets from it.
2.5.5	Broadcast the current state of the float switch periodically to allow sumppi to obtain it.

## Operational
The Table below details the operational capabilities required of the software during the prototype deployment. Only developers will be required to access the system.
Table 4: Operational Requirements

No	Requirement
3.3.1	It shall be possible to monitor the system operation by logging in from a laptop or mobile phone.
3.3.2	It shall be possible to copy results from the master or remote Pi for later study.
3.3.3	It shall be possible to copy files from a laptop or mobile phone to the master or remote Pi to allow updating.

## Documentation
The Table below details the documentation requirements for the software.
Table 5: Documentation Requirements

No	Requirement
3.4.1	A comprehensive design specification shall be produced.
3.4.2	The design specification shall include full descriptions of all functionality of all components of the software.
3.4.3	All software shall be fully documented with comments.

# ASSUMPTIONS
The following assumptions are made.
Developers will have the pre-requisite knowledge to design and implement the software required to realise this stage of the project and subsequently enhance it.

Annex A - Illustrations

Sump Area
Butts Area
PSU
240 V AC
to
 19 V DC
DC-DC
Converter
19 V DC
to
 5 V DC

240 V AC in

Raspberry Pi
Zero

PoE
Injector

PoE
Splitter

Cat 5

DC-DC
Converter
19 V DC
to
 5 V DC

Level
Converter
/ Buffers
5 V DC
to
3.3 V DC
From Sensor Probe

10

10

USB /
Ethernet
Adaptor

5 V in
USB

GPIO

Cat 5
19 V DC

Raspberry Pi
Zero

Level
Converter
/ Buffers
5 V DC
to
3.3 V DC
From Sensor Probe or Float Switch

10

10

USB /
Ethernet
Adaptor

5 V in
USB

GPIO

Cat 5

Level
Converter
/ Buffers
3.3 V DC
to
5 V DC
To Butts Pump SSR

GPIO
WiFi AP
&
Switch

Notes:
1. This diagram to be read in conjunction with the Butts Pi and Sump Pi Layout Diagrams.
2. Initial deployment will have no Levels Sensor at the Butts; just a Float Switch.
3. For final deployment, the WiFi AP will be removed and the Sump Pi connected to the
     Cat 5 side of the PoE Injector.
Illustration 1: River System – Prototype Butts / Sump Arrangement