Max/Min float switch theory of operation
For clarity the sketches on this page show the two parts of the device separately. These sketches also show and describe the float switch parts in their normal operating condition, ie the water level is above minimum and below maximum
Max. level sensor
In operation between the max and min water levels the max level micro-switch is kept ‘closed’ by the mass of the counter-weight acting through the actuator. The micro-switch requires around 70g to ‘close’ it.
In this condition the Common and Normally Open terminals of the Max. micro-switch are shorted together.
micro-switch
actuator
counter-weight
float
stand-pipe
water level
Min. level sensor
In operation between the max and min water levels the min level micro-switch is kept ‘open’ by the return spring within the micro-switch holding the actuator up, the float is boyant in this condition and the coupling is slack.
In this condition the Common and Normally Closed terminals of the Min. micro-switche are shorted together.
Flexible non-elastic coupling

---
- water level above max.
For clarity the sketch on this page show only the max. portion of the device.
When the water level exceeds max. the float pushes against the underside of the actuator and lifts it upward, allowing the micro-switch’s return spring to ‘open” its contacts.
The float must be boyant enough to overcome the mass of the couter-weight and actuator.
In this condition the Common and Normally Close terminals of the Max. micro-switch are shorted together.

---
- water level below min.
For clarity the sketch on this page show only the min. portion of the device.
When the water level is less then min. the coupling prevents the float from displacing enough volume of water to remain buoyant and are a result the float exerts a downward force on the actuator, this causes the micro-switch to close.
The float must have enough mass to overcome the return spring within the micro-switch. Around 70g is required to close the micro-switch.
The length of the coupling determines where the min. water level is
In this condition the Common and Normally Open terminals of the Max. micro-switch are shorted together.

---
-sketch of complete assembly
min. micro-switch
max. micro-switch
wooden chassis
6 mm OD brass tube
Fixed to chassis as bearing
2 mm OD brass tube
Max. actuator
4 mm OD brass tube
Min, actuator
Flexible non-elastic coupler (fishing line)
weight in float